## Sheet1
PLW SYSTEM SIZING |  |  |  | CONSTANTS |  | WORKINGS
|  |  |  | CAL | 4.2
INPUTS: (User Entered Values) |  |  |  | LITRE | 1000 | J/DAY | 25416000
Consumption | 120 | (Litres/day) |  | JOULE/KWH | 3600000 | J/TOT | 38124000
Usable Water Temp | 42 | (degC) | User comfort level |  |  | DELTA T | 28
Input Water Temp | 13 | (degC) | Use worst case in winter |  |  | CALORIES REQ | 9077142.8571
Peak Sun Hours per day | 3 |  | Worst case from insolation map |  |  | CC req | 324183.6735
Thermostat Temp | 70 | (degC) | Max 70 degC for Enamel tanks |  |  | litres req | 324.1837
Tank Loss per day | 3 | (kwh/day) | See your tank data sheet
Days of Autonomy | 1.5 | (days) | How many days with poor sun (Sets tank size)
OUTPUTS: (Calculated Results)
Energy Needed | 7.06 | (kWh/day) | Average
Array Size | 2.3533 | (kW) | Minimum
Tank Size | 324.1837 | (Litres) | Recommended
NOTES:
Max load current = 30A
Using the 2.5 ohm element supplied with the PLW that means max 30A of 72 cell modules = 3 strings at 9A/string = 6 modules
With 62 cell modules, the load current is limited by voltage and max solar current is 80A, = 9 strings = 18 modules
Winter is usually worst case by a big margin, so install panels on a high winter angle.
Tank info can be found here : http://reg.energyrating.gov.au/comparator/product_types/58/search/
Insolation (Sun) Map: http://www.plasmatronics.com.au/downloads/Insolation_MapWeb_BP.pdf